## Ph-II Schedule
Name of the Work: Construction of Kolkata Police Training Academy at Kamardanga, Howrah.(Phase II) - Supply, Installation, Testing and Commissioning of Electro- Mechanical Components Sewage Treatment Plant
Item No. | Description of Item. | Unit. | Quantity
1 | Supply, Installation, Testing and Commissioning of Electro- Mechanical Components Sewage Treatment Plant as per specifications, drawings and as per process of treatment with accessories complete operational : | LS | 1
• Non clog sewage pumps with suitable motors of 8.3m3 / hr capacity of 10m. pumping head - 5Nos (Three Working + Two Standby).
.Level Switch in Inlet Sump , Equalisation Tank, Filter Feed Tank, Sludge Holding Tank & Treated Water tank for control of transfer pumps and high level alarm - 5 Nos.
. • Internal and Discharge UPVC piping in Sewage Sump- 1 Lot.
• Rotary Twin Lobe type Air Blowers of 265m3 / hr (approx) at a pressure 0.4 kg/cm2 capacity - 2 Nos (One Working + One Standby).
• Air Header and Sub Header Piping - 1 Lot.
• Air Diffusers - 1 Lot.
• Valves for Aeration Piping and Others - 1 Lot.
• Sludge Recirculation Pumps of 7m3 / hr capacity of 15 m. pumping head - 2 Nos (One Working + One Standby).
• Chlorination System : 2 nos. Chlorine Dosing System with HDPE / PVC Tank of 100 Ltrs. capacity with suitable arrangement for Chlorine dosing in Chlorine contact tank
• Filter Feed & Backwash Pumps of 7m3 / hr capacity of 25 m. WC pumping head - 2 Nos (One Working + One Standby).
• Multi grade filter of capacity 7m3 / hr ; -1 No.
FRP Vessel (762mm.dia x 2032mm.ht.) with UPVC Valves and pipeline
• Activated Carbon Filter of capacity 7m3/hr. - 1 No.
FRP Vessel (762mm.dia x 2032mm.ht.) with UPVC Valves and pipeline
• Sludge Feed Pump with electric drives of 1m3 / hr capacity of 50 m. Discharge head -1 Set (1 Feed Pump & 1 Boosting pump)
• Filter Press of 10 kg/batch capacity - 1 No.
• Liquid Recycling Sump of Volume 2.0 Cum - 1 No (Customer’s Scope).
• Liquid Recycling Sump Pump of Capacity 2m3/hr of 10M WC Pumping Head - 1 No
• Bacteria culture for stabilisation
• Valves / Fittings - 1 Lot.
• Pressure Gauges - 1 Lot.
• Flow Measuring Device of Rota meter - 1 No.
• Control Panel for Pumps, Blowers etc - 1 No.
• Control & Power Cables for Pumps, Blowers, Filter Press etc. - 1 Lot.
• Gate Valves, Non- return Valves, Butterfly Valves, Level Switches, Effluent Quality Monitors, required lenghts of UPVC Pipe Sch. 40 with fittings, Electrical power cables, control wires, Electrical Control Panels - 1 Lot

## Rate Ana.
Rate Analysis of Concrete (M30 Grade Design Mix) for ''Construction of Kolkata Police Training Academy near Kamardanga STP area in the district of Howrah(Phase-ll)".
Sl.No | Item Description
1 | Supplying ready mixed concrete of M 30 Grade with well graded stone chips of 20 mm nominal size containing designed quantity of cement per Cu.m of wet concrete produced in computerised batching plant under controlled condition using approved super plastisizer, designing concrete mix following I.S. 10262 and I.S. 456, transporting the mix with agitation in transit mixer to work site depositing the mix on a platform erected for the purpose at required levels of concreting and then placing the mix in its final location of form work compacting and curing the same complete as per specification & direction of the Engineer-in-charge including computerised batching plant transit mixer with all accessories vibrators etc. inclusive of all other incidental charges in this connection complete but excluding cost of hire charge of platform and its supporting staging which would be paid through separate item. [cement to be supplied by the Manufacturer/supplier] - Foundation & Ground Floor (Page no: 21 & Item no: 09B (c) ii) With approved concrete pump.
| Item Description |  |  | Rate | Amount | Cumulative Amount | Ref. No. | Remarks
A | Rate of item as per relevant section of this schedule |  | Rs. | 6786 | 6786 |  | P - 23, I - 9B(c) (ii)
|  |  | Rs. | Total | 6786 | 6786 | Consider Salimar yard and distance from site is assumed 9.0 km
B | Rates of Pakur varity stone aggregates at different railway yards from Table : T-1
| 20 mm nominal size | 0.54 | Rs. | 1520 | 820.8 | 820.8 | P-312 Table: T-1
| 10 mm nominal size | 0.36 | Rs. | 1353 | 487.08 | 487.08 | P-312 Table: T-1
| Total | 0.9 | Rs. | Total | 1307.88 | 1307.88
C | Carriage works and Transportation for 0.86 CuM. Stone Aggregates at distance 5 Km.
| Upto 5 Km |  | Rs. | 124 | 124 |  | P-315
| Above 5 Km TO 9 Km. |  | Rs. | 10.9/Km. | 43.6 |  | Table: T-2
|  |  | Rs. | Total | 167.6 | 150.84
D | Loading and Unloding by Manual means | 0.9 | Rs. | 58 | 52.2 |  | P-316 Table: T-3 | (58*0.9,2) = 52.2
|  |  | Rs. | Total | 52.2 | 52.2
| Analysed Concrete rate |  |  |  | Rs. | 8296.92 | (A+B+C+D)

## Rate Ana. NS
Construction of Kolkata police Training Academy near Kamardanga STP area in the district of Howrah(Phase-ll)
RATE ANNALYSIS
Non Schedule Supplementary Item No. | Description of Item. | VALUE IN RS. | Unit. | Remarks.
RATE ANALYSIS (Basic Rate considered from Market)
NS2/1.00 | Sewage Treatment Plant
Construction in RCC, including all earth work, de-watering if required of the following Chambers/tanks as per specifications, Drawings and Design as per the process of treatment, including shade , puddle collars, sleeves . Inserts, manholes, water proofing, surface finishing & painting etc., and plants and accessories all complete operational:
• Inlet Sump chamber - 1 No
1.5m x 1.5m x 2.5m (SWD)
• Bar Screen chamber - 1 No
1.0m x1.0m x 1.5m (SWD)
• Grit chamber (Detritus Tank) - 1 No.
1.0m x 1.0m x 1.5m SWD.
• Oil and Grease chamber - 1 No.
1.0m x 1.0m x 1.5m SWD.
• Raw Sewage Equalisation Tank - 1 No.
33 cum capacity (for process requirement of 200 cum/hr. capacity STP, operating depth may be fixed up by suitable setting of level switch).
• Aeration Tank - 1 No.
165 cum capacity
• Clarifier Tank, Lamella / Tube Settler - 1 No.
55 Cum capacity
• Chlorine Contact Tank - 1 no.(to be covered with RCC Roof)
19.8 cum capacity
• Sludge Sump - 1 No.
49.5 cum capacity
• Treated Sewage Collection Sump -1 no. (to be covered with RCC Roof)
Treated Water Tank
33 cum capacity
Construction of Operators Room (including partitioned Filtered Press Room) and housing of MCC panel, Motors, Blowers etc. Clear internal ht. approx . 3 m from floor level. In RCC frame structure with shade and brick walls, One no. Door (3m x 2.4m ht), two no windows including floor.
Providing, Installation, Testing and Commissioning of the following Electro-mechanical equipments, machineries and materials as per specifications, Drawings, as per process of treatment with accessories complete operational :
• Non clog sewage pumps with suitable motors of 8.3m3 / hr capacity of 10m. pumping head - 5Nos (Three Working + Two Standby).
.Level Switch in Inlet Sump , Equalisation Tank, Filter Feed Tank, Sludge Holding Tank & Treated Water tank for control of transfer pumps and high level alarm - 5 Nos.
. • Internal and Discharge UPVC piping in Sewage Sump- 1 Lot.
• Rotary Twin Lobe type Air Blowers of 265m3 / hr (approx) at a pressure 0.4 kg/cm2 capacity - 2 Nos (One Working + One Standby).
• Air Header and Sub Header Piping - 1 Lot.
• Air Diffusers - 1 Lot.
• Valves for Aeration Piping and Others - 1 Lot.
• Sludge Recirculation Pumps of 7m3 / hr capacity of 15 m. pumping head - 2 Nos (One Working + One Standby).
Chlorination System :
2 nos. Chlorine Dosing System with HDPE / PVC Tank of 100 Ltrs. capacity with suitable arrangement for Chlorine dosing in Chlorine contact tank
• Filter Feed & Backwash Pumps of 7m3 / hr capacity of 25 m. WC pumping head - 2 Nos (One Working + One Standby).
• Multi grade filter of capacity 7m3 / hr ; -1 No.
FRP Vessel (762mm.dia x 2032mm.ht.) with UPVC Valves and pipeline
• Activated Carbon Filter of capacity 7m3/hr. - 1 No.
FRP Vessel (762mm.dia x 2032mm.ht.) with UPVC Valves and pipeline
• Sludge Feed Pump with electric drives of 1m3 / hr capacity of 50 m. Discharge head -1 Set (1 Feed Pump & 1 Boosting pump)
• Filter Press of 10 kg/batch capacity - 1 No.
• Liquid Recycling Sump of Volume 2.0 Cum - 1 No (Customer’s Scope).
• Liquid Recycling Sump Pump of Capacity 2m3/hr of 10M WC Pumping Head - 1 No
• Bacteria culture for stabilisation
• Valves / Fittings - 1 Lot.
• Pressure Gauges - 1 Lot.
• Flow Measuring Device of Rota meter - 1 No.
• Control Panel for Pumps, Blowers etc - 1 No.
• Control & Power Cables for Pumps, Blowers, Filter Press etc. - 1 Lot.
• Gate Valves, Non- return Valves, Butterfly Valves, Level Switches, Effluent Quality Monitors, required lenghts of UPVC Pipe Sch. 40 with fittings, Electrical power cables, control wires, Electrical Control Panels - 1 Lot
| Providing & installation of Sewage treatment plant of capacity 200 KLD as per above specification. | 3063200
| Profit @10% | 306320
| Total | 3369520
| GST @12% | 404342.4
| TOTAL | 3773862.4 | Per Job
NS2/2.00 | Operation & maintenance of the plant for One years from the date of completion including cost of all consumables and required manpower deployed during Operation & Maintenance period (cost of power, water, Guest House/Quarter for the operator will be borne by the customer) – 1 job
Payment – Monthly basis.
| Basic Rate per month | 39200
| Profit @10% | 3920
| Total | 43120
| GST @12% | 5174.4
| TOTAL | 48294.4 | Per Month

## fin
Financial Implication for Excess Execution / Supplementary Works / Substitute Supplementary in connection to the following works.
1 | Description of work | :- | Construction of Kolkata Police Training Academy at Kamardanga, Howrah.Phase-II)
2 | Name of the Executing Agency | :- | M/S Mackintosh Burn Limited.
3 | Estimated cost put to tender | Rs. | 940159042
4 | Tender Agreement no. | :- | 14/ADG(H)/E-1 of 2018-2019
5 | Tender Amount | Rs. | 845296994
6 | Amount of sanctioned
| i) Supplymentary Tender | Rs. | 16229548.47
| ii)Supplementary tender due to substitute of work | Rs. | 0
| iii)Supplementary excess quantity of work | Rs. | 0
7 | Amount of proposed. | :-
| a)Supplymentary tender | Rs. | #REF!
| b)Substitute supplementary tender | Rs. | 0
| c)Excess quantity | Rs. | 0
8 | Amount of work already paid (R.A.) | Rs. | 157379017.13
9 | Further likely cost of remaining work | Rs. | 782780024.87
10 | Total likely work including ST & excess | Rs. | 940159042
11 | % of total Effective S.T. on the Tendered amount | :- | #REF!
12 | % of total Effective S.S.T. on the Tendered amount | :- | 0%
13 | % excess of total value of work On the Estimated amount put to tender. (SL. NO.10-SL. NO.3) X 100/SL. NO.3 | :- | 0%